Workpaper SCGWP 091116 C

Revision 2

Southern California Gas Company

Customer Programs Department

Title

Natural Gas Chiller Replacement Program for units up to 100 tons

Double Effect Absorption 25-100 tons

This work paper is for SCG Programs ONLY

Work Paper Created By:	Cypress Ltd:

Tom Smolarek

Gordon Broberg

Paul Delaney

7 Rue Delacroix

Coto de Caza, CA  92679

(949) 888-0255

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| 1 | Feb 1, 2008 | Gas Cool Double Effect Absorption 25 -100 tons | Same |
| 2 | Nov 16, 2009 | Gas Cool Double Effect Absorption 25 - 100 tons | Same |

Measure Summary Table

| Measure Name | Work Paper RunID: WPSCXXXXXXXX- | CZ | Target Sector | Measure Electric End Use Shape (Load Shape) | EUL or RUL E3 Name: Measure Type (To Look up Measure Life) | NTG E3 Name: Program Type (To Look Up Net-to-Gross Ratio) | Unit Definition | Program Type (NEW, ROB, RET) | Gross Measure Cost ($/unit) | Incremental Measure Cost ($/unit) | Gas Savings (Therms) | Gross Unit Annual Electricity Savings (kWh/unit) | User Entered kW Savings per unit (kW/unit) | % Eligible for TOU AC Adjustment | Total Number of Units | Gross Realization Rate (GRR) | Delivery Methods) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 25-100 ton double effect gas abs | N/A | 6 | Office |  | 18 |  | Ton | RET | 900 | 400 | 173 |  |  |  | 534 |  |  |
| 25-100 ton double effect gas abs | N/A | 8 | Office |  | 18 |  | Ton | RET | 900 | 400 | 198 |  |  |  | 592 |  |  |
| 25-100 ton double effect gas abs | N/A | 9 | Office |  | 18 |  | Ton | RET | 900 | 400 | 205 |  |  |  | 592 |  |  |
| 25-100 ton double effect gas abs | N/A | 10 | Office |  | 18 |  | Ton | RET | 900 | 400 | 215 |  |  |  | 592 |  |  |
| 25-100 ton double effect gas abs | N/A | 14 | Office |  | 18 |  | Ton | RET | 900 | 400 | 208 |  |  |  | 591 |  |  |
| 25-100 ton double effect gas abs | N/A | 15 | Office |  | 18 |  | Ton | RET | 900 | 400 | 267 |  |  |  | 593 |  |  |

# Table of Contents

Revision History	i

Measure Summary Table	ii

List of Figures	v

List of Tables	v

Section 1.	General Measure & Baseline Data	1

1.1	Measure & Delivery Description	1

1.2	DEER Differences Analysis	3

1.3	Code Analysis	3

1.4	Measure Effective Useful Life	3

1.5	Net-to-Gross Ratios for Different Program Strategies	3

1.6	Gross Realization Rate	3

1.7	Time-of-Use Adjustment Factor	3

Section 2.	Energy Savings & Demand Reduction Calculations	3

Section 3.	Load Shapes	3

Section 4.	Base Case & Measure Costs	4

4.1	Base Case Cost	4

4.2	Gross Measure Cost	4

Gross Measure Data	4

4.3	Incremental Measure Cost	4

Attachments	5

References	6

Table and Figure Titles	7

List of Figures

List of Tables

General Measure & Baseline Data

EnergyPro modeling software was the primary tool used to determine the energy savings for this measure.  A generic office model for pre-1978 buildings was created and used to simulate cooling loads in each of the climate zones.  DEER v2.1 office building guidelines and default software values were used as guides for the following basic parameters:

| 10,000 sqft, equal sides 2 floors Pre-1978 equivalent roof, flat Pre-1978 equivalent walls 40% window to wall area single-pane metal frame windows | 9 foot ceiling height 12 foot wall height slab foundation Occupancy 100 sqft/person Lighting density -1.2 watts/sqft Receptacle loads – 1.5 watts/sqft. cooling set point – 76’F |
| --- | --- |

The “old” double effect gas absorption (COP-0.6) simulation was run first, and the cooling load and annual energy usage was determined.  Then the “new” unit (COP-1.0) simulation was run.  Energy savings per ton was then calculated using the following equation:

(ENERGY USAGE old ÷ COOLING LOAD old ) –

(ENERGY USAGE new ÷ COOLING LOAD new ) = THERMS/TON

ENERGY USAGE = Btu

COOLING LOAD = ton

TON = 12,000 Btu/ton

Simulations were then run for the old and new gas cooling units.  Natural gas savings was calculated using the above equation.

Measure & Delivery Description

All sources for the entries in these summary tables are cited in the pertinent sections of the Work Paper and should not be repeated in the summary tables.

| Natural Gas Chiller Replacement Program for Units up to 100 tons: | Replace existing less efficient gas chillers with efficient double effect absorption. |
| --- | --- |
| Savings Impacts Common Units: | Refrigerant Tons (RT) |
| Base Case Description: | Single effect natural gas absorption COP .35 |
| Costs Common Units: | Same as Savings Impacts |
| Measure Equipment Cost ($/unit): | The equipment cost of the energy efficiency measure. |
| Measure Incremental Cost ($/unit): | In this program the incremental cost is equal to the measure equipment cost.. |
| Measure Installed Cost ($/unit): | The total of the measure equipment and installation labor costs. |
| Effective Useful Life (years): | 18 years |
| Program Type: | Early Retirement (RET) |
| Net-to-Gross Ratios: | NTG used is .8 (non-DEER listed default value) |
| Comments: | Customer options are limited to available product. |

Gas Savings

| Unit of Measure | Building Type | Building Vintage | Climate Zone6 | Gross Annual Nat. Gas Savings (therms/unit) |
| --- | --- | --- | --- | --- |
| Tons | Office | <1978 | 6 | 173 |
| Tons | Office | <1978 | 8 | 198 |
| Tons Tons Tons Tons | Office Office Office Office | <1978 <1978 <1978 <1978 | 9 10 14 15 | 205 215 208 267 |

Measure Data

| Unit of Measure | Program Strategy | Base Equipment Cost | Measure Equipment Cost | Incremental Cost | Labor Cost | Installed Cost |
| --- | --- | --- | --- | --- | --- | --- |
| Double effect absorption per ton | RET | N/A | $900/ton | $900/ton | $400/ton | $1300/ton |

- Measure Description:  Early retirement and replacement of old gas chillers with new high efficiency double effect gas absorption chillers in the 25-100 ton range for the small commercial market.

Gas cooling units are installed in small businesses throughout the SCG service territory.  These units are old and may fail soon, so customers are entering the market to replace the units.  The market share for gas cooling has been on the decline over the years due to a variety of factors including rising gas rates, lower costs for the electric alternative product, high equipment prices for the gas units, limited product choice (few manufacturers) poor market strategy by the upstream players, and lack of quality assurance for the product and lack of qualified installers. This program will work to ensure the replacement of these old existing units and transition to new high efficiency gas AC equipment instead of alternative technologies.

Cypress believes it is in the best interest of the natural gas industry to continue to serve its customer base that has opted for gas cooling product in the past by continuing to serve this market through the promotion of newer more efficient equipment and by working to improve the quality of installations and service by working with the manufacturers, distributors, and contractors that provide the product to the end use customer. Cypress believes this program can improve both the economics and quality control aspects of gas cooling while providing energy savings for SCG and its customers.

DEER Differences Analysis

Note: This is a non-DEER measure. Gas cooling is not listed. Natural gas chillers are not included in the DEER  database.

Code Analysis

N/A Program is currently limited to retrofit only. Gas cooling products are listed in the California Energy Commission Title 20 Appliance Standards

Measure Effective Useful Life

| Effective Useful Life (years): | 18 years |
| --- | --- |

This is the same as typical HVAC equipment Retrofit

(RET) – replacing a working technology prior to failure.

Net-to-Gross Ratios for Different Program Strategies

| Net-to-Gross Ratios: | NTG used is .8 (non-DEER listed gas equipment default value) |
| --- | --- |

Gross Realization Rate

N/A no M&V studies where found to demonstrate this Rate

Time-of-Use Adjustment Factor

N/A  Gas measure

Energy Savings & Demand Reduction Calculations

N/A  Gas measure– This measure will not impact electrical load as currently defined as a gas cooling replacement program.

Load Shapes

This measure will not impact electrical load.

Base Case & Measure Costs

- Base case for the gas cooling program are determined by an estimated degradation factor of the customers current equipment. That is a COP of .35 for absorption equipment and .60 for gas engine driven equipment. New equipment meets or exceeds minimum efficiencies as listed in California Title 20 Appliance Standards. Energy Pro analysis for typical residential and commercial applications have been developed as a means of estimating energy savings.

Base Case Cost

Base case measure costs include the cost of the equipment from the contractor to the customer and installation or labor charges. The costs do not include upgrades to ducting or plumbing system or any costs that are not directly related to the change out of the cold generator. Confidential cost estimates were compiled from the market channel and include inputs from manufacturers, distributors ,and contractors. These include  installation cost estimates were taken from industry contractors and distributors. Confidential cost estimates were provided by United Air Conditioning in Yorba Linda, Darrow Heating & Air in North Hollywood, Mediterranean Heating & Air in Canoga Park, Thermal Comfort Systems, in Northridge and Howard Industries in Culver City, and Summit Energy. All quotes confidential.

Gross Measure Cost

- Gross Measure Data

Measure Data

| Unit of Measure | Program Strategy | Base Equipment Cost | Measure Equipment Cost | Incremental Cost | Labor Cost | Installed Cost |
| --- | --- | --- | --- | --- | --- | --- |
| Double effect absorption per ton | RET | N/A | $900/ton | $900/ton | $400/ton | $1300/ton |

Incremental Measure Cost

The incremental costs and the full measure costs are the same for this program as the alternative measure is a fuel switch to electric cooling as opposed to a higher level of incremental energy efficiency of the measure type which is not available.

Attachments

None
References

- DEER Measure Cost Users Guide

- Energy Pro 4.4 Building Energy Simulation Software, EnergySoft LLC, Martyn Dodd

- 2005 Building Energy Efficiency Standards for residential and nonresidential buildings, CEC, October 1, 2005.

Table and Figure Titles

Note: COP old unit efficiency ratings are estimates based on industry experts. The primary source for determining degradation factors was Conservation Technology, Mr Ying Yu who has considerable expertise in monitoring and installation of monitoring equipment for gas cooling.